## Index
Inspection and test plans
20 plans, one per sheet. Project Audit Pro · projectauditpro.com · free to use and to change
Each plan lists the activities, what is being checked against, the acceptance criteria, and the point type. Fill in the shaded columns on site.
Ref | Plan | Discipline | Governing standards | Stages
ITP-01 | Substructure & Below-ground Drainage | Civils | BS 8000-1 (excavation & filling), BS 8000-14 (below-ground drainage), BS EN 1610 | 7
ITP-02 | Masonry & External Envelope | Structure / Envelope | BS 8000-3 (masonry), BS EN 1996, NHBC Standards Chapter 6.1 | 7
ITP-03 | Roofing & Waterproofing | Envelope | BS 8000-4 (waterproofing), BS 8000-6 (slating & tiling), BS 5534, BS 8217/8747 | 7
ITP-04 | Windows, External Doors & Curtain Walling | Envelope | BS 8213-4, BS 6375, BS 8000-7 (glazing) | 7
ITP-05 | Partitions, Drylining & Fire-stopping | Fit-out | BS 8000-8 (plasterboard partitions & dry lining), BS 8214, ASFP guidance | 7
ITP-06 | Plastering & Rendering | Finishes | BS 8000-10 (plastering & rendering), BS EN 13914 | 6
ITP-07 | Screeds & Floor Finishes | Finishes | BS 8000-9 (screeds & toppings), BS 8204, BS 5385 (tiling beds) | 6
ITP-08 | Carpentry, Joinery & Second Fix | Fit-out | BS 8000-5 (carpentry, joinery & general fixings), BS 8214 (fire doors) | 7
ITP-09 | Ceramic, Stone & Mosaic Tiling | Finishes | BS 8000-11.1 / 11.2, BS 5385 parts 1–5 | 6
ITP-10 | Decoration & Wallcoverings | Finishes | BS 8000-12 (decorative works), BS 6150 | 6
ITP-11 | Sanitaryware & Above-ground Drainage | M&E / Fit-out | BS 8000-13 (sanitary appliances & above-ground drainage), BS EN 12056 | 6
ITP-12 | Hot & Cold Water Services | M&E | BS 8000-15 (hot & cold water services), Water Supply (Water Fittings) Regulations, BS 8558 | 7
ITP-13 | Electrical Installation & Testing | M&E | BS 7671 (IET Wiring Regulations), Approved Documents P, M and B | 7
ITP-14 | Sealants, Joints & Airtightness | Envelope / Finishes | BS 8000-16 (sealing joints with sealants), BS 6213, Approved Document L | 5
ITP-15 | Testing, Commissioning & Pre-handover | Cross-discipline | Project commissioning specification, Approved Documents F, L and B, Building Safety Act 2022 (HRB) | 7
ITP-16 | Suspended Ceilings (MF Grid Systems) | Fit-out | BS 8290 (suspended ceilings — code of practice), BS 8000-8 (dry lining board fixing) | 7
ITP-17 | Dot & Dab Drylining | Fit-out | BS 8000-8 (dry lining board fixing), BS 8212 (dry lining & partitioning using gypsum plasterboard) | 6
ITP-18 | SFS External Wall Framing | Structure / Envelope | FIS SFS Specifiers Guide (light gauge steel framing — external wall systems), BS EN 1993-1-3 (design of cold-formed steel), manufacturer system approval | 8
ITP-19 | Door Ironmongery (per door set) | Fit-out | BS 8214 (fire door assemblies — code of practice), BS EN 1935 / BS EN 1154-1155 (hinges and controlled door closing devices), approved door and ironmongery schedule | 9
ITP-20 | Internal Door Installation (per door set) | Fit-out | BS 8214 (fire door assemblies — code of practice), BS 8000-5 (carpentry, joinery and general fixings), approved door schedule | 9

## Point types
Point types
The four letters used in the Type column.
Type | Means | What it obliges
H | Hold point | Work must not proceed past this point until the named party has inspected and released it.
W | Witness point | The named party is given notice and may attend. Work may proceed if they do not.
I | Inspection point | Inspected and recorded by the contractor. No external release needed.
S | Surveillance | Monitored over time rather than at a single moment — a daily or batch record.

## ITP-01 Substructure & Below-gro
ITP-01 — Substructure & Below-ground Drainage
BS 8000-1 (excavation & filling), BS 8000-14 (below-ground drainage), BS EN 1610
Project |  | Location / unit
Contractor |  | ITP number | ITP-01
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Setting out verified against drawings | Positions, levels and dimensions to approved GA | Approved setting-out drawing | Within ±10 mm of drawing dimensions; datum confirmed | I | Site Manager | Setting-out record
2 | Excavation formation inspected | Bearing stratum as designed, clean and free of soft spots | SI report / SE instruction | Formation accepted in writing by Structural Engineer before covering | I | Structural Engineer | Formation approval
3 | Reinforcement inspection prior to pour | Bar size, spacing, laps and cover to drawings | RC detail drawings | Cover within tolerance; no displaced or contaminated bars | I | Structural Engineer | Pre-pour checklist + photos
4 | Concrete delivery and testing | Correct mix, slump and cube samples taken | Delivery tickets, BS EN 206 | Mix matches spec; cubes taken at agreed frequency; 28-day results compliant | I | Site Manager | Delivery tickets, cube results
5 | Drainage laid to line, level and fall | Gradients, bedding and surround as specified | Drainage layout, BS 8000-14 | Falls within design tolerance; correct bedding class; no ponding | I | Site Manager | Level record
6 | Drainage air / water test before backfill | System tested to BS EN 1610 | BS EN 1610 | No failure of the test over the specified period; retest after remedial | I | Building Control | Test certificate
7 | Backfill and compaction | Material and layer thickness as specified | BS 8000-1 | Compacted in specified layers; no oversize or unsuitable material | S | Site Manager | Backfill record

## ITP-02 Masonry & External Envel
ITP-02 — Masonry & External Envelope
BS 8000-3 (masonry), BS EN 1996, NHBC Standards Chapter 6.1
Project |  | Location / unit
Contractor |  | ITP number | ITP-02
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Materials delivered and stored correctly | Correct blocks/bricks, mortar designation, protection from weather | Approved material submittal | Matches approved sample; stored off ground and covered | I | Site Manager | Delivery record + photo
2 | DPC and cavity trays installed | Correct height, laps and dressing | BS 8215, detail drawings | DPC min 150 mm above finished ground level; laps sealed; trays with stop ends | I | Site Manager | Photo register
3 | Wall ties — type, spacing and embedment | Density and embedment as designed | BS EN 845-1, drawings | Correct type and spacing; minimum embedment both leaves; ties clean and sloping outward | I | Site Manager | Tie inspection sheet
4 | Cavity insulation continuity | Full fill / partial fill boards fitted without gaps | Manufacturer instructions | No gaps, boards butted and retained; cavity clear of mortar droppings | I | Site Manager | Photo register (pre-close)
5 | Plumb, level and gauge of masonry | Workmanship tolerances | BS 8000-3, NHBC tolerances | Verticality and line within permitted deviation; consistent joint gauge | I | Site Manager | Dimensional check sheet
6 | Movement joints and lintels | Positions, bearings and joint widths as designed | Structural drawings | Lintel end bearings achieved; movement joints at designed centres and unobstructed | I | Structural Engineer | Inspection record
7 | Pointing and weathering | Joint profile consistent, no voids | BS 8000-3 | Full joints, consistent profile and colour, no smears to face | I | Site Manager | Photo record

## ITP-03 Roofing & Waterproofing
ITP-03 — Roofing & Waterproofing
BS 8000-4 (waterproofing), BS 8000-6 (slating & tiling), BS 5534, BS 8217/8747
Project |  | Location / unit
Contractor |  | ITP number | ITP-03
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Substrate / deck inspection before covering | Falls, fixings and dryness of deck | Roof layout and falls drawing | Designed falls achieved, no ponding areas, deck sound and dry | I | Site Manager | Pre-cover record
2 | Vapour control layer and insulation | Continuity, laps and fixings | Manufacturer system detail | Laps to manufacturer minimum, sealed; insulation tight-butted, no gaps | I | Manufacturer Rep | Photo register
3 | Membrane / covering installation | Installed by approved operative to system detail | System warranty conditions | Welds/seams continuous and probe-tested; correct overlaps at upstands | W | Manufacturer Rep | Installer sign-off
4 | Upstands, terminations and outlets | Minimum upstand heights, correct outlets and clamping | BS 8000-4, system detail | Upstands to specified minimum height; outlets clamped and clear | I | Manufacturer Rep | Photo record
5 | Tiling/slating — batten gauge, fixings and underlay | Fixing specification for wind zone | BS 5534, fixing spec | Batten gauge and fixings as calculated; underlay laps correct; no torn membrane | I | Site Manager | Inspection sheet
6 | Flood / water test | Watertightness demonstrated | Project specification | No leakage after the specified test duration | I | Client Rep | Test certificate
7 | System guarantee issued | Manufacturer inspection and warranty | Warranty conditions | Written guarantee received and filed in O&M | A | Manufacturer Rep | Guarantee document

## ITP-04 Windows, External Doors
ITP-04 — Windows, External Doors & Curtain Walling
BS 8213-4, BS 6375, BS 8000-7 (glazing)
Project |  | Location / unit
Contractor |  | ITP number | ITP-04
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Survey and schedule verification before order | Structural opening sizes checked against schedule | Window schedule / quotation | Every opening measured; couplers and corner connectors allowed for; deviations flagged before manufacture | I | Site Manager | Dimensional check sheet
2 | Delivery inspection | Correct units, glazing spec and finish, undamaged | Approved order and schedule | Frame finish, glass spec, U-value and safety glazing per schedule; no transit damage | I | Site Manager | Delivery inspection sheet
3 | Fixing and packing to structure | Fixing type, centres and packers as specified | Manufacturer fixing detail | Fixings at specified centres, packed at load points, frame square and plumb | I | Site Manager | Inspection record
4 | Perimeter sealing and weathering | Continuous internal and external seals | BS 8000-16, detail drawings | Continuous seal both faces, correct backing rod, no gaps at cills or jambs | I | Site Manager | Photo register
5 | Safety glazing and critical locations | Marked safety glass in critical locations | Approved Document K, BS 6206 | Permanent marks visible and compliant in every critical location | I | Building Control | Glass mark photo record
6 | Operation, ironmongery and restrictors | Smooth operation, correct restrictors and locks | Ironmongery schedule | All opening lights operate and lock; restrictors fitted where required | I | Site Manager | Operation checklist
7 | Water penetration / hose test on sample | Weathertightness of installed sample | BS 6375-1 / CWCT sequence B | No water penetration to inside face during test | W | Client Rep | Test record

## ITP-05 Partitions, Drylining &
ITP-05 — Partitions, Drylining & Fire-stopping
BS 8000-8 (plasterboard partitions & dry lining), BS 8214, ASFP guidance
Project |  | Location / unit
Contractor |  | ITP number | ITP-05
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Setting out of partitions | Line and position to approved layout | Approved GA layout | Positions within tolerance; door openings and structural openings correct | I | Site Manager | Setting-out record
2 | Framing, head deflection and fixings | Stud gauge, centres, deflection head detail | System spec, BS 8000-8 | Correct stud gauge and centres; deflection head allowance provided at soffit | I | Site Manager | Inspection sheet
3 | Acoustic / fire insulation installed | Correct density and full fill | Acoustic and fire strategy | Specified product, tight fit, no gaps at perimeters or services | I | Site Manager | Photo register (pre-close)
4 | Boarding — layers, orientation and fixings | Board type, number of layers, staggered joints | System certified detail | Board type/thickness per fire test evidence; joints staggered; fixings at specified centres | I | Building Control | Board inspection sheet
5 | Service penetrations fire-stopped | Every penetration sealed with a tested system | Third-party certified detail | Correct product and depth; each penetration photographed, labelled and logged | I | Fire Consultant | Fire-stopping register + photos
6 | Compartment line continuity above ceilings | Compartmentation continuous to slab soffit | Fire strategy drawing | No unsealed voids at compartment lines; cavity barriers installed | I | Fire Consultant | Photo register
7 | Jointing, taping and finish level | Finish level as specified | BS 8000-8 | Specified finish level achieved; no visible fastener heads, ridges or beading | I | Site Manager | Finish inspection

## ITP-06 Plastering & Rendering
ITP-06 — Plastering & Rendering
BS 8000-10 (plastering & rendering), BS EN 13914
Project |  | Location / unit
Contractor |  | ITP number | ITP-06
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Background preparation and suction control | Background clean, sound and correctly prepared | BS 8000-10 | Background free of dust, laitance and contaminants; suction controlled as required | I | Site Manager | Pre-start check
2 | Beads, stops and reinforcement | Correct type, alignment and fixing | Detail drawings | Beads plumb and true; corrosion-resistant type used; mesh at junctions of dissimilar backgrounds | I | Site Manager | Inspection record
3 | Mix, coat thickness and curing | Mix proportions and coat thicknesses to spec | BS 8000-10, manufacturer data | Thickness within specified range; no application in unsuitable conditions; protected while curing | S | Site Manager | Daily record
4 | Flatness and surface regularity | Deviation under a 2 m straightedge | Project specification | Within the specified tolerance under a 2 m straightedge; no hollowness on tap test | I | Site Manager | Straightedge check sheet
5 | Junctions, reveals and services boxes | Neat, square and consistent | BS 8000-10 | Reveals square and plumb; boxes flush and not proud; no shrinkage cracking at junctions | I | Site Manager | Snag pre-check
6 | Final surface handover to decorator | Surface accepted as ready to decorate | Trade interface agreement | Signed acceptance by following trade before decoration starts | I | Site Manager | Trade handover sheet

## ITP-07 Screeds & Floor Finishes
ITP-07 — Screeds & Floor Finishes
BS 8000-9 (screeds & toppings), BS 8204, BS 5385 (tiling beds)
Project |  | Location / unit
Contractor |  | ITP number | ITP-07
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Substrate preparation and DPM | Clean, sound base with DPM/separating layer where designed | BS 8204, floor build-up detail | DPM continuous and lapped up perimeter; base free of debris and contaminants | I | Site Manager | Pre-pour photo record
2 | Insulation, UFH pipework and edge strips | Layout, fixings and pressure test before covering | UFH layout drawing | UFH pressurised and holding before and during pour; edge insulation continuous | I | M&E Engineer | Pressure test record
3 | Screed mix, thickness and reinforcement | Mix, minimum thickness and mesh as specified | BS 8204 | Minimum thickness achieved over pipes/insulation; correct mix and any specified fibres | I | Site Manager | Pour record
4 | Surface regularity and level | SR classification as specified | BS 8204-1 | Meets the specified surface regularity class; levels within tolerance of datum | I | Site Manager | Level survey
5 | Drying and moisture test before covering | Relative humidity test to BS 8203 | BS 8203 / BS 5325 | RH at or below the floor covering manufacturer limit before laying | I | Site Manager | Hygrometer test certificate
6 | Floor covering installation and protection | Adhesive, setting out and expansion allowances | Manufacturer instructions | No hollowness, lipping within tolerance, movement joints coincident with structure | I | Site Manager | Inspection record

## ITP-08 Carpentry, Joinery & Sec
ITP-08 — Carpentry, Joinery & Second Fix
BS 8000-5 (carpentry, joinery & general fixings), BS 8214 (fire doors)
Project |  | Location / unit
Contractor |  | ITP number | ITP-08
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Moisture content and storage of joinery | Timber conditioned to in-service moisture content | BS 8000-5 | Moisture content within specified range; stored flat, dry and protected | I | Site Manager | Moisture readings
2 | Fire door sets — leaf, frame and certification | Certified door set matched to opening | BS 8214, third-party cert | Label/plug present; leaf, frame and ironmongery from the tested configuration | I | Fire Consultant | Fire door register
3 | Fire door installation — gaps, intumescent, closers | Gaps and seals to certification | Third-party installation instruction | Perimeter gaps within certified tolerance; intumescent and smoke seals continuous; door closes and latches from any position | I | Fire Consultant | Fire door inspection sheet
4 | Ironmongery installation | Schedule compliance, operation and handing | Ironmongery schedule | Correct item and finish per door; smooth operation; no packing behind hinges | I | Site Manager | Door-by-door checklist
5 | Skirtings, architraves and trims | Scribes, mitres and fixings | BS 8000-5 | Tight mitres and scribes, no open joints; fixings punched and filled; level and true | I | Site Manager | Inspection record
6 | Kitchen and wardrobe installation | Level, plumb, secure and to layout | Approved kitchen layout | Carcasses level and plumb; doors aligned with consistent shadow gaps; worktop joints sealed | I | Site Manager | Unit checklist
7 | Staircase, balustrade and guarding | Guarding heights and gap limits | Approved Document K | Guarding height and 100 mm sphere rule satisfied; balustrade rigid under load | I | Building Control | Dimensional check

## ITP-09 Ceramic, Stone & Mosaic
ITP-09 — Ceramic, Stone & Mosaic Tiling
BS 8000-11.1 / 11.2, BS 5385 parts 1–5
Project |  | Location / unit
Contractor |  | ITP number | ITP-09
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Background suitability and tanking | Background sound, flat and correctly primed; wet areas tanked | BS 5385, tanking system data | Tanking continuous with correct laps at junctions and around penetrations, allowed to cure | I | Site Manager | Photo register (pre-tile)
2 | Setting out and tile selection | Approved setting out; tiles from batched deliveries | Approved setting-out drawing | Cuts balanced and no slivers at focal points; shade batches mixed to avoid banding | I | Client Rep | Setting-out approval
3 | Adhesive type and bed coverage | Correct adhesive class and solid bed | BS 5385, adhesive data sheet | Solid bed coverage — no voids on lift test; correct adhesive class for substrate and location | I | Site Manager | Lift test record
4 | Falls to drainage in wet areas | Positive fall to gullies/trays | Detail drawings | Water drains fully to outlet with no ponding after flood test | I | Site Manager | Water test record
5 | Grouting and movement joints | Grout type, joint widths and movement joint positions | BS 5385-1 & -3 | Movement joints at specified centres and at all internal corners; grout full and consistent | I | Site Manager | Inspection record
6 | Silicone sealing and finish inspection | Neat continuous seals at all junctions | BS 8000-16 | Continuous, evenly tooled seals; no lipping between tiles beyond tolerance; no hollow tiles on tap test | I | Site Manager | Snag pre-check

## ITP-10 Decoration & Wallcoverin
ITP-10 — Decoration & Wallcoverings
BS 8000-12 (decorative works), BS 6150
Project |  | Location / unit
Contractor |  | ITP number | ITP-10
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Surface acceptance before decoration | Preceding trade surface accepted in writing | Trade interface agreement | Signed acceptance; surfaces filled, sanded and dust-free | I | Site Manager | Trade handover sheet
2 | Moisture content of substrate | Substrate dry enough to decorate | BS 6150 | Within the coating manufacturer stated limit for the substrate | I | Site Manager | Moisture readings
3 | Materials and colour approval | Approved products, colours and sheen levels | Finishes schedule, approved sample | Matches approved sample panel; correct system for the location | I | Client Rep | Sample panel sign-off
4 | Primer / sealer coat | Correct primer for substrate applied | Manufacturer system | Full coverage, correct product, recorded before subsequent coats | I | Site Manager | Coat record
5 | Coat build and drying times | Number of coats and intervals as specified | Manufacturer data sheet | Specified number of coats applied with correct overcoating intervals | S | Site Manager | Daily record
6 | Final finish inspection under working light | Uniform finish, cut-in lines and edges | BS 8000-12 | Even opacity with no roller marks, flashing, runs or misses; sharp cut-in lines; no overspill on ironmongery or glass | I | Client Rep | Room-by-room snag sheet

## ITP-11 Sanitaryware & Above-gro
ITP-11 — Sanitaryware & Above-ground Drainage
BS 8000-13 (sanitary appliances & above-ground drainage), BS EN 12056
Project |  | Location / unit
Contractor |  | ITP number | ITP-11
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Appliance and brassware verification | Products match approved FFE schedule | FFE / sanitary schedule | Model, finish and handing per schedule; undamaged on delivery | I | Site Manager | Delivery inspection
2 | Concealed pipework and noggins before boarding | Routes, supports and fixings before closing up | M&E layout | Pipework supported at specified centres, insulated where required, noggins in place | I | M&E Engineer | Photo register (pre-close)
3 | Soil and waste falls and trap seals | Gradients and seal depths | BS EN 12056-2 | Falls within design range; trap seals to standard; no unvented long branches | I | M&E Engineer | Inspection record
4 | Appliance fixing, levels and sealing | Secure, level and sealed to adjacent finishes | BS 8000-13 | Rigid with no movement; level; continuous neat silicone to junctions | I | Site Manager | Unit checklist
5 | Air test on above-ground drainage | System pressure tested | BS EN 12056-2 | System holds the specified pressure for the specified period | I | Building Control | Test certificate
6 | Function test — fill, flush and drain | Every appliance operated | Commissioning schedule | No leaks under running conditions; full flush and drain; no cross-flow between appliances | W | Client Rep | Commissioning sheet

## ITP-12 Hot & Cold Water Service
ITP-12 — Hot & Cold Water Services
BS 8000-15 (hot & cold water services), Water Supply (Water Fittings) Regulations, BS 8558
Project |  | Location / unit
Contractor |  | ITP number | ITP-12
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Materials and fittings approval | WRAS/approved fittings and correct pipe grades | Approved M&E submittal | All fittings approved for potable use; no unapproved components | I | M&E Engineer | Material register
2 | Pipework routes, supports and insulation | Support centres, expansion and insulation thickness | BS 8000-15, M&E spec | Supports at specified centres; insulation continuous and correct thickness; frost protection where needed | I | M&E Engineer | Inspection sheet
3 | Backflow prevention and stopcocks | Correct fluid category protection and isolation | Water Fittings Regulations | Correct device for the fluid category; isolation valves accessible and labelled | I | M&E Engineer | Inspection record
4 | Pressure test before concealment | System tested and held | BS 8558 | No pressure drop over the specified test period; test witnessed before closing up | I | Client Rep | Pressure test certificate
5 | Unvented cylinder installation and G3 | Installed and commissioned by competent person | Approved Document G3 | Discharge pipework compliant, safety devices set and benchmark completed | I | M&E Engineer | G3 / benchmark certificate
6 | Flushing, disinfection and sampling | System cleaned and sampled | BS 8558 / HSG274 | Chlorination and flushing records complete; sample results within limits | I | M&E Engineer | Chlorination + sample certificates
7 | Temperature and flow rate commissioning | Outlet temperatures and flows recorded | Commissioning schedule | Temperatures and flow rates within design ranges at every outlet | W | Client Rep | Commissioning sheet

## ITP-13 Electrical Installation
ITP-13 — Electrical Installation & Testing
BS 7671 (IET Wiring Regulations), Approved Documents P, M and B
Project |  | Location / unit
Contractor |  | ITP number | ITP-13
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Design and load assessment approval | Approved schematic, load and protective device schedule | Approved M&E design | Design approved before first fix; device ratings and discrimination confirmed | I | M&E Engineer | Design approval
2 | First fix — routes, zones, depths and fire-stopping | Cables in permitted zones with correct protection | BS 7671 Section 522 | Cables in prescribed zones or mechanically protected; penetrations fire-stopped and logged | I | M&E Engineer | Photo register (pre-close)
3 | Accessory heights and positions | Positions per Approved Document M and layouts | Approved Document M, layouts | Switch and socket heights within the required range; positions match layout | I | Site Manager | Room-by-room check
4 | Earthing and bonding | Main and supplementary bonding as designed | BS 7671 Chapter 54 | Correct conductor sizes; connections tight, labelled and accessible | I | M&E Engineer | Inspection record
5 | Smoke, heat and CO detection | Grade, category, positions and interlink | BS 5839-6 | Correct grade and category for the dwelling; devices interlinked and positioned per standard | I | Building Control | Detection commissioning sheet
6 | Inspection and testing to BS 7671 | Full initial verification | BS 7671 Part 6 | All test results within limits; no departures unless recorded and justified | I | M&E Engineer | Schedule of test results
7 | Electrical Installation Certificate issued | EIC and schedules under a competent-person scheme | Approved Document P | EIC issued, signed and notified; copy filed in O&M | I | M&E Engineer | EIC + notification

## ITP-14 Sealants, Joints & Airti
ITP-14 — Sealants, Joints & Airtightness
BS 8000-16 (sealing joints with sealants), BS 6213, Approved Document L
Project |  | Location / unit
Contractor |  | ITP number | ITP-14
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Joint preparation and backing | Joint clean, dry and correctly sized with backing rod | BS 8000-16 | Correct width-to-depth ratio; backing rod fitted; no bond on three faces | I | Site Manager | Pre-seal check
2 | Sealant selection and primer | Correct sealant for movement and substrates | Manufacturer data | Sealant rated for the joint movement; primer used where the data sheet requires it | I | Site Manager | Material record
3 | Application and tooling | Full, continuous and tooled | BS 8000-16 | No voids, gaps or slumping; even tooled profile; adjacent surfaces clean | I | Site Manager | Photo record
4 | Air barrier continuity survey | Continuous line of airtightness | Airtightness strategy drawing | No unsealed service penetrations, junctions or perimeter gaps on the air barrier line | I | Site Manager | Pre-test survey + photos
5 | Air permeability test | Test to the design target | ATTMA TSL1 / Approved Document L | Result at or below the design air permeability target | I | Building Control | Air test certificate

## ITP-15 Testing, Commissioning &
ITP-15 — Testing, Commissioning & Pre-handover
Project commissioning specification, Approved Documents F, L and B, Building Safety Act 2022 (HRB)
Project |  | Location / unit
Contractor |  | ITP number | ITP-15
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Ventilation commissioning and airflow rates | Measured rates against Part F requirements | Approved Document F, commissioning sheet | Measured airflow at or above the required rate at every terminal | I | Building Control | Part F commissioning sheet
2 | Heating system balance and controls | Balanced flow and correct control strategy | M&E commissioning spec | Design temperatures achieved; zones and controls operate as designed | W | M&E Engineer | Commissioning record
3 | Fire alarm and emergency lighting commissioning | Full cause-and-effect demonstration | BS 5839, BS 5266 | All devices operate; cause and effect matrix demonstrated and signed | I | Fire Consultant | Commissioning certificate
4 | Fire-stopping register complete and verified | Every penetration recorded and photographed | Third-party certified details | 100% of penetrations logged with photo, product, date and installer | I | Fire Consultant | Fire-stopping register
5 | As-built information and O&M compiled | Complete O&M and as-built set | Contract requirements | All certificates, warranties, as-builts and product data received and indexed | I | Client Rep | O&M index
6 | Golden thread records uploaded (HRB) | Digital building safety information handed over | Building Safety Act 2022 / BR 2010 Part 2A | Records accurate, current, secure and accessible to the Accountable Person before occupation | I | Client Rep | Golden thread transfer record
7 | Pre-handover joint inspection | Joint walk with client representative | Contract completion procedure | Agreed snag list issued and all items closed before certification | I | Client Rep | Joint inspection sheet

## ITP-16 Suspended Ceilings (MF G
ITP-16 — Suspended Ceilings (MF Grid Systems)
BS 8290 (suspended ceilings — code of practice), BS 8000-8 (dry lining board fixing)
Project |  | Location / unit
Contractor |  | ITP number | ITP-16
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Preceding trade handover and area clearance | Area cleared of materials, no unresolved clashes with services or acoustic hanger design | Trade interface agreement, services co-ordination drawing | Signed handover from preceding trade; clashes resolved before hanger fixing starts | I | Site Manager | Trade handover sheet
2 | Hanger pattress and primary suspension fixed and levelled | Fixing centres and hanger type per system design | Manufacturer system detail | Hangers at specified centres, fixed to structure per pattress design, level within tolerance | I | Site Manager | Pre-close photo register
3 | MF suspension grid installed to datum | Grid centres and datum level as designed | Ceiling layout / datum drawing | Grid at correct centres; datum confirmed by level check before boarding starts | I | Site Manager | Datum check sheet
4 | Service void closure before boarding | Void closed / fire-stopped where compartment lines cross the ceiling | Fire strategy drawing | No unsealed voids at compartment lines before the ceiling is closed up | I | Fire Consultant | Photo register (pre-close)
5 | Boarding — layers, joints and datum | Board type, layer count and joint stagger as specified | System certified detail | Correct board type/thickness per fire test evidence where fire-rated; joints staggered between layers; datum maintained | I | Building Control | Board inspection sheet
6 | Pelmets, trims and access panels installed | Pelmet lines straight and level; access provided where designed | Ceiling layout drawing | Straight, level pelmet lines; an access panel at every designed service access point | I | Site Manager | Inspection record
7 | Handover to following trade | Ceiling accepted as ready for decoration / services final fix | Trade interface agreement | Signed acceptance by the following trade before their work starts | I | Site Manager | Trade handover sheet

## ITP-17 Dot & Dab Drylining
ITP-17 — Dot & Dab Drylining
BS 8000-8 (dry lining board fixing), BS 8212 (dry lining & partitioning using gypsum plasterboard)
Project |  | Location / unit
Contractor |  | ITP number | ITP-17
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Preceding trade handover and background check | Background sound, clean and ready to receive adhesive | Trade interface agreement | Signed handover; background free of loose material, dust and high spots | I | Site Manager | Trade handover sheet
2 | Setting out verified | Board layout and reveal returns per drawing | Approved layout drawing | Setting out within tolerance; reveals and openings correctly positioned before dabbing starts | I | Site Manager | Setting-out record
3 | Adhesive dab pattern and coverage | Continuous dabs at perimeters, correct spacing across the board face | Manufacturer system data | Dabs continuous at skirting level, ceiling level and all internal/external reveals; no voids leaving an edge unsupported | I | Site Manager | Photo register (pre-decoration)
4 | Board fixing — square, plumb and true | Boards square, plumb and true to line | BS 8000-8 | Boards square and true; plumb within tolerance; no rocking or drumminess on tap test once cured | I | Site Manager | Inspection sheet
5 | Trims and beads | Angle beads and trims fixed per detail | Manufacturer detail | Beads plumb, true and fully bedded; no exposed cut edges | I | Site Manager | Inspection record
6 | Handover to following trade | Surface accepted as ready for jointing/decoration | Trade interface agreement | Signed acceptance by the following trade before jointing starts | I | Site Manager | Trade handover sheet

## ITP-18 SFS External Wall Framin
ITP-18 — SFS External Wall Framing
FIS SFS Specifiers Guide (light gauge steel framing — external wall systems), BS EN 1993-1-3 (design of cold-formed steel), manufacturer system approval
Project |  | Location / unit
Contractor |  | ITP number | ITP-18
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Setting out and base track inspection | Base track level, dimensions and substrate condition verified before fixing | Approved setting-out / GA drawing | Setting out correct to the latest approved drawing; base track surfaces checked for level, dimensional accuracy and damage before fixing | I | Site Manager | Setting-out record
2 | Materials and components approval | SFS components and accessories match the approved system, undamaged | Approved system submittal | Correct specification, no substitutions, free from damage on delivery | I | Site Manager | Delivery inspection sheet
3 | Framing installed to correct location and centres | Metal framing location, centres, brick-tie support and movement joint positions as designed | Manufacturer system drawings | Framing location verified by the subcontractor; correct centres; brick tie supports and movement joints at designed positions | I | Site Manager | Frame inspection sheet
4 | Deflection head and design movement allowance | Deflection allowance, depth and slab movement as designed | Structural / system design | Deflection head installed to design and specification, with the agreed depth and slab movement allowed for | I | Structural Engineer | Deflection head inspection
5 | Apertures, openings and service penetrations | Openings formed per door/window schedules, including service penetrations, to approved design | Door and window schedules, approved system design | Every opening and penetration formed per schedule; sufficient photographs taken for record purposes before close-up | I | Site Manager | Photo register (pre-close)
6 | Weather defence board and fixings | Board line, level and screw centres as specified | Manufacturer fixing detail | Weather defence boards to correct line and level at the outer edge; screws at correct centres; mastic paste applied to all joints and screw heads | I | Site Manager | Inspection sheet
7 | EPDM breather membrane installation | Membrane laps and continuity as designed | Manufacturer system detail | Approved EPDM installed per design with a minimum 100 mm overlap; continuous bead of mastic to the EPDM ensuring a watertight seal | I | Site Manager | Photo register
8 | Clear and handover to following trade | Area cleared, ready for the following trade (external skin or internal lining) | Trade interface agreement | Signed acceptance by the following trade before their work starts | I | Site Manager | Trade handover sheet

## ITP-19 Door Ironmongery (per do
ITP-19 — Door Ironmongery (per door set)
BS 8214 (fire door assemblies — code of practice), BS EN 1935 / BS EN 1154-1155 (hinges and controlled door closing devices), approved door and ironmongery schedule
Project |  | Location / unit
Contractor |  | ITP number | ITP-19
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Preceding trade handover and area clearance | Door set installed, area cleared and ready for ironmongery | Trade interface agreement | Signed handover from the preceding trade; area clear of materials before work starts | I | Site Manager | Trade handover sheet
2 | Setting out taken from the approved ironmongery schedule | Component heights and positions per the door and ironmongery schedule | Architect's door and ironmongery schedule | Setting out taken from the current issue of the schedule, not from a previous door | I | Site Manager | Setting-out record
3 | Ironmongery issued checked against the schedule | Items issued for this door match the schedule item for item | Door and ironmongery schedule, delivery note | Every item present, correct reference and finish, undamaged; any substitution approved in writing before fitting | I | Site Manager | Ironmongery check sheet
4 | Fire-rated ironmongery certification | Hinges, closers, locks and seals compatible with the door's fire test evidence | Door set certification, product certificates | Every item on a fire door carries evidence of compatibility with that door set; no uncertified substitution | I | Building Control | Certificate pack
5 | Items installed and door operation checked | Door operates freely, latches and closes correctly, free of obstruction | Manufacturer fitting instructions | Door swings, latches and (where fitted) self-closes fully from any angle; no binding on frame, floor or seals | I | Site Manager | Operation check
6 | Items removed for decoration and stored | Ironmongery removed where the door is to be painted, boxed and stored | Site procedure | Items removed, boxed, labelled per door and returned to secure storage — not left loose on site | I | Site Manager | Storage register
7 | Reinstated after decoration and outstanding items completed | All ironmongery refitted once decoration is complete | Door and ironmongery schedule | Every item on the schedule fitted and working; nothing left outstanding | I | Site Manager | Ironmongery check sheet
8 | Cylinders installed, tagged and keys issued | Lock cylinders fitted, keys tagged and handed to the block manager | Keying schedule / master suite | Cylinder matches the keying schedule; keys tagged to the door number and issued against signature | I | Client Rep | Key issue receipt
9 | Snag, clear and hand over to the following trade | Installed works snagged, area cleared | Trade interface agreement | Snag list raised and closed; materials cleared; signed acceptance by the following trade | I | Site Manager | Trade handover sheet

## ITP-20 Internal Door Installati
ITP-20 — Internal Door Installation (per door set)
BS 8214 (fire door assemblies — code of practice), BS 8000-5 (carpentry, joinery and general fixings), approved door schedule
Project |  | Location / unit
Contractor |  | ITP number | ITP-20
Shaded cells are yours to fill in. Result: Pass, Fail or N/A.
No. | Activity | What is checked | Reference | Acceptance criteria | Type | Verified by | Record | Result | Comment / reference | Date | Signed
1 | Preceding trade handover, clearance and conditions | Area cleared and at the temperature required for installation | Trade interface agreement, manufacturer fitting instructions | Signed handover; area clear; ambient conditions within the range the door manufacturer allows before doors are unwrapped | I | Site Manager | Trade handover sheet
2 | Door number checked against the plan before fitting | The right door set in the right opening | Approved door schedule and floor plan | Door reference confirmed against the schedule and the plan before the set is fitted — fire rating and handing included | I | Site Manager | Door schedule check
3 | Door set examined for defects before fitting | Leaf and frame undamaged, correct specification, certification label intact | Door set certification | No damage, distortion or missing certification label; any defective set rejected rather than fitted | I | Site Manager | Delivery / pre-fit inspection
4 | Structural opening checked against frame size | Opening dimensions suit the frame with the gaps the certification allows | Door schedule, door set certification | Opening within tolerance; frame plumb, square and level once fixed | I | Site Manager | Opening check sheet
5 | Fixings and packers | Fixings at the centres the certification requires, correctly packed | Manufacturer fitting instructions | Fixings at the specified centres; packers a minimum of 10 mm back from the frame face on both sides and left in place at every fixing | I | Site Manager | Fixing inspection
6 | Perimeter seal to fire door frames | Frame-to-structure gap sealed to the certified detail | Door set certification, fire strategy | Fire mastic to the frame perimeter, gap no more than 8 mm — expanding foam is not acceptable on a fire door | I | Fire Consultant | Photo register (pre-architrave)
7 | Gaps, floor clearance and closing | Leaf-to-frame and threshold gaps within the certified range | BS 8214, door set certification | Head and stile gaps and floor clearance within the tested tolerance, measured and recorded, not judged by eye | I | Building Control | Gap measurement record
8 | Ironmongery fitted and operation checked | Ironmongery per the design specification, door operated to prove the installation | Door and ironmongery schedule | Items fitted per specification; door opens, latches and closes correctly (see ITP-19 for the full ironmongery sequence) | I | Site Manager | Operation check
9 | Defects check and protection applied | Door protected against damage from following trades | Site procedure | Defects recorded before protection goes on; protection applied and intact at handover | I | Site Manager | Protection record